Somerset Rural Electric Cooperative, Inc.

# 223 Industrial Park Rd

Somerset, PA   15501

814-445-4106       800-443-4255

# General Requirements for Service

- Requirements for Service:

- The following items must be completed prior to any work being performed by Somerset Rural Electric:

- Membership Application: Must be filled out properly and returned to the Cooperative.

- Right-of-Way Agreement: Must be filled out, signed by property owner(s) as name appears on deed, notarized, and returned to the Cooperative. This document can be notarized at the Cooperative for your convenience.

- Primary Installation Requirements:

- Overhead single-phase line extension: Member is responsible for the initial clearing of rights-of-way. A minimum 40-foot ground to sky right-of-way is required. (20 ft. on each side of line)

- Underground single-phase line extension: Member is responsible for providing a 48-inch-deep ditch and 4-inch gray schedule 40 PVC the full length of the ditch with a pull rope in the conduit (conduit pull tape or a minimum ¼ inch nylon rope is required). The conduit will need to be bedded in 6” of dust, sand, or clean fill above and below. (to the discretion of the Cooperative; check with the Staking Engineer) At each end of pipe, a 90-degree long sweeping elbow is required.

  - A 5’x 5’ x 30” transformer pit is required with the 90-degree sweep positioned in the center of the 5’x 5’ pit.

  - A minimum one-foot vertical separation between our cable and the phone and/or cable TV is required.

  - Neither water, septic, nor gas lines are permitted in the same ditch.

  - The ditch must be backfilled with at least one foot of material before the cable can be energized.

  - The Cooperative will provide red warning ribbon that the member will be required to install in the ditch 1 ft. above the conduit.

  - An inspection of the ditch may be required before backfilling takes place.

- Secondary Installation Requirements:

- The meter base location must be located outside and accessible to Cooperative employees.

- Equipment and materials for standard service requests (100, 200, and 400-amp) are generally readily available. For larger service requests (greater than 400-amp), acquiring equipment and materials may involve longer lead times.

- Secondary overhead service requires a minimum of 10 ft. cleared right-of-way is required. (5 ft. on each side of line)

- 200-amp secondary underground service: A 200-amp underground style meter base is the minimum size permitted for underground services even when a 100-amp disconnect, or breaker panel is used.

- 400-amp secondary underground service: A 400-amp self-contained meter base with lugs (lugs that will accept up to 500 mcm conductor) is required. In addition, the meter base must be equipped with a load bypass.

- For all secondary underground services, whether it is coming from a pole mounted, or pad mounted transformer, the member is responsible for all ditching, conduit, pull tape or rope and slip joint, also referred to as meter socket riser, PVC expansion coupling, or Carlon Slip Meter Riser fitting, and the meter socket.

- Secondary Underground Installation:

For both 200-amp and 400-amp underground services the member is required to provide a 30-inch-deep ditch and 3-inch gray schedule 40 electrical conduit the full distance of the ditch, with a pull rope in the conduit (conduit pull tape or a minimum ¼ inch nylon rope is required). At each end of the pipe, 90-degree long sweeping elbows are required.

  - A 3-inch schedule 80 conduit and a slip joint from the elbow to the meter socket is required.

  - Conduit will be bedded in 12 inches of dust, sand, or clean fill (6 inches above and 6 inches below the conduit to the discretion of the Cooperative: discuss with Staking Engineer).

  - A minimum one-foot vertical separation between our cable and the phone and/or cable TV is required.

  - Neither water, septic, nor gas lines are permitted in the same ditch.

  - The Cooperative will provide red warning ribbon which the member will install on top of the 12 inches of bedding prior to backfilling. Prior to energizing the cable, a minimum of 1 foot of material must be backfilled over the conduit.

In the case where the meter base is not permitted to be mounted to the structure, such as a Mobile Home, Trailer, or for a Temporary Service, the member is responsible for supplying a meter base disconnect support structure (power pedestal). The minimum support structure shall consist of a treated 6x6 post buried a minimum of 36 inches in the ground with the meter socket located approximately 5 feet above ground level, or a backboard can be built with a minimum of two treated 4x4 posts buried a minimum of 36 inches in the ground using treated lumber to tie the two posts together and secure the meter base disconnect on it.

  - The support structure (power pedestal) is the property of the member, and the member is responsible for the upkeep and integrity of the structure.

Electrical Inspection: All new services must be inspected. See partial list of electrical inspectors included in this packet (not limited to these).

Temporary Service:  $200 (non-refundable fee; no materials/equipment included).

Mobile Home and Trailer Connections: Credit must be established by applicants for all mobile homes and trailer connection services where the unit is not placed on a permanent foundation. If credit is not established the applicant is required to provide a $200 deposit.

Yard Light: Available to all co-op members. A LED light can be mounted on a Somerset REC pole for $13/month. This option can be discussed further with the Staking Engineer upon site visit.

- Field Visit:

Once the initial paperwork is completed and sent back to the Cooperative, a Staking Engineer will be in contact to discuss the new service. In the meantime, if there are any questions regarding the new service, please contact the Cooperative and ask to speak with a Staking Engineer.

John Hochard    			     Zack Pritts

- Solar Installations - All questions regarding residential solar projects should be directed to Emily Baer, Director of Marketing and Member Services, at ebaer@somersetrec.com or 814-445-4106. An interconnection application and FAQs regarding solar interconnections is also available on our website.

- Generator Information – The cooperative does not install generators and we do not carry Generac products. The device offered by the co-op is called a GenerLink. This unit is available for purchase and is installed directly behind the meter, providing a safer connection between your generator and panel.

**LOCATIONS OF PROPOSED ELECTRIC FACILITIES BOTH OVERHEAD AND UNDERGROUND MUST MEET SREC APPROVAL PRIOR TO THE START OF CLEARING OR DIGGING FOR SUCH FACILITIES. THIS INCLUDES BUT NOT LIMITED TO DITCHES, TRANSFORMERS, AND METERING POINTS. CALL THE COOPERATIVE TO DISCUSS OR SCHEDULE A MEETING WITH ONE OF OUR STAKING ENGINEERS. **

This document is for your reference only and is intended to be viewed as additional information to all local, state, and federal laws. The contents within this document are subject to change.

If you have any questions, please don't hesitate to contact the Cooperative at:

Address: 223 Industrial Park Road, Somerset, PA 15501

Telephone: (814) 445-4106

Toll Free: 1-800-443-4255

Fax: (814) 445-5526

Website: www.somersetrec.com

E-Mail: service@somersetrec.com